DIESEL GENERATING SET

MPS0250IVC-3

|  |  | Standby Rating |  |  | Prime Rating |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Voltage | Phase | kWe | kVa | Amps | kWe | kVa | Amps | p.f. |
| 120/208 | 3 | 250 | 313 | 867 | 225 | 281 | 781 | 0.8 |
| 277/480 | 3 | 250 | 313 | 375 | 225 | 281 | 339 | 0.8 |
| 347/600 | 3 | 250 | 313 | 300 | 225 | 281 | 271 | 0.8 |

STANDARD GENERATING SET FEATURES

| ▪ water cooled engine | ▪ single bearing alternator | ▪ stainless steel exhaust bellows |
| --- | --- | --- |
| ▪ oil & fuel filters | ▪ 3 pole circuit breaker | ▪ set mounted starting batteries |
| ▪ lube oil drain valve | ▪ auto start control panel | ▪ operation & maintenance manual |
| ▪ 12 V dc starter and alternator | ▪ low coolant level shutdown | ▪ factory tests |
| ▪ electronic governor | ▪ welded steel base frame | ▪ 2 yr / 2000 hour warranty |
| ▪ standard duty air filter | ▪ integral vibration isolators |  |

GENERATING SET PERFORMANCE

| Voltage Regulation | Optimized Electrical Design | Alternator Temperature Rise |
| --- | --- | --- |
| ▪ +/- 1% voltage regulation | ▪ 4 pole brushless, 2/3 pitch winding | ▪ class H insulation |
|  | minimizing harmonic distortion for |  |
| Frequency Regulation | increased parallel operation | Design Specifications |
| ▪ isochronous from no load to 100% load | performance | ▪ the alternator meets NEMA MG-1-32 |
| with electronic governor | Random Frequency Variation | BS5000, CSA C22.2 and IEC 34 |
|  | ▪ RTF not to exceed +/- 0.2% of its mean | requirements |
|  | value for no load to full load |  |

ENGINE SPECIFICATIONS

| FPT/Iveco | Fuel System | Oil System |
| --- | --- | --- |
| ▪ C87 TE1D, EPA Tier III | ▪ common rail fuel system | ▪ closed crankcase vent |
| ▪ in line 6 cylinder engine | ▪ fuel filter | ▪ oil filter |
| Type | ▪ water separator | ▪ 600 hour oil change interval |
| ▪ water cooled 4 cycle turbocharged and | Starting | Cooling |
| air to air aftercooled | ▪ 12Vdc starter | ▪ 55oC radiator |
|  | ▪ 45A battery charging alternator | ▪ pusher fan |

ALTERNATOR SPECIFICATIONS

| ▪ brushless single bearing, revolving field | ▪ 12 lead connectable alternator | ▪ heavy duty bearing |
| --- | --- | --- |
| ▪ 4 pole, drip proof, screen protected | (6 lead for 347/600V) | (minimum life of 100,000 hours) |
| ▪ class H insulation |  | ▪ direct flange mounted for proper |
|  |  | alignment |

COMPLIANCE STANDARDS

The generating set complies with ISO 3046 & ISO 8528

STANDBY POWER RATING (ESP)

The standby power rating is applicable for supplying emergency power for the duration of the utility power outage.  No overload, utility parallel or negotiated power outage operation capability is available at this rating.  In installations served by unreliable utility sources (where outages last longer or occur more frequently), where operation is likely to exceed 200 hours per year, the Prime Power rating should be applied.  The Standby Power rating is only applicable for emergency and standby applications where the generating set serves as the back up to the normal utility source.

PRIME POWER RATING (PRP)

Prime power is available for an unlimited number of hours per year in a variable load application, in accordance with ISO8528-1.  A 10% overload capability is available for a period of 1 hour with a 12 hour period of operation, in accordance with ISO 3046-1.  Variable load should not exceed a 70% average of the Prime Power rating during any operating period of 250 hours.

Technical Data 								 MPS0250IVC-3

|  | Standby | Prime |  | Standby | Prime |
| --- | --- | --- | --- | --- | --- |
| Engine Make | FPT/Iveco |  | Oil Pan Capacity | 23 L |  |
| Engine Model | C87 TE1D |  | Oil Change Interval | 600 h |  |
| Configuration | In-line 6 |  | Exhaust flow | 56.8 m3/min | 51.1 m3/min |
| Displacement | 8.7L |  | Exhaust temp | 500 oC | 486 oC |
| Bore & Stroke | 117mm x 135mm |  | Max exhaust back press | 5 kPa |  |
| Aspiration | turbocharged air to air aftercooled |  | Ambient Temperature | 55 oC |  |
| Power kWm (bhp) | 276 (370) | 254 (340) | Engine Coolant Capacity | 15 L |  |
| Governor | Electronic |  | Total Coolant Capacity | 63 L |  |
| Starting | 24Vdc |  | Radiator Cooling Air | 390 m3/min | 363 m3/min |
| Charging Alternator | 24Vdc, 45A |  | Combustion Air | 20.8 m3/min | 19.2 m3/min |
| Alternator Make | Newage/Stamford |  | Recommended Fuel | # 2 diesel |  |
| Model | UCI274J |  | Fuel Consumption |  |  |
| Temperature Rise | 125 oC |  | 100 % | 72.3 L/hr | 64.3 L/hr |
| Insulation | Class H |  | 75 % | 54.2 L/hr | 48.2 L/hr |
| Bearing | Single |  | 50 % | 38.8 L/hr | 34.1 L/hr |
| Voltage regulation | +/- 1.0 % |  | 25 % | 20.2 L/hr | 18.0 L/hr |

DIMENSIONS & WEIGHTS

|  | Length (A) | Width (B) | Height (C) | Weight |
| --- | --- | --- | --- | --- |
| Open | 3000 mm | 1170 mm | 1795 mm | 2600 kg |
| Silent* | 4000 mm | 1288 mm | 2150 mm | 3840 kg |

*not including sub-base fuel tank

GENERATING SET OPTIONS

| Engine | Control | Others |
| --- | --- | --- |
| □ Heavy Duty Air Filter | □ Paralleling EasyGen 2000 |  |
| □ Air Cleaner Restriction Indicator | □ Expanded Paralleling EasyGen 3000 |  |
| □ Manual Oil Drain Pump | □ Remote Annunciator |  |
| □ Oil Pan Heater | □ Utility Grade Protective Relaying |  |
| □ Coolant Heater & Thermostat | □ Remote Emergency Stop |  |
| Alternator | Electrical |  |
| □ Anti-Condensation Heaters | □ Starting Batteries |  |
| □ Increased Motor Starting | □ Battery Charger |  |
| □ PMG Excitation | □ Battery Blankets |  |
| □ Double Bearing | □ Multiple Circuit Breakers |  |
| □ Tropical Insulation Protection | □ 100% Circuit Breakers |  |
| Fuel | □ LSI(G) Trip Plugs |  |
| □ Flexible Fuel Lines | Exhaust |  |
| □ Fusible Fire Valve | □ Critical Silencer (15-20 dBA) |  |
| □ Sub-base Double Walled Fuel Tanks | □ Hospital Silencer (20-25 dBA) |  |
| □ Day Tank with Automatic Pumping | □ Hospital Plus Silencer (25-30 dBA) |  |

Specifications may change without notice.  Check with your distributor for more information                                                                                                                  www.madsen.ca

Toronto : 30 Voyager Court South- (416) 907-3844 Sarnia : 469 Polymoore Drive, Corunna - 519) 330-7387 Quebec : 96 Avenue Leacock, Pointe-Claire - (514) 971-2063 Alberta : 2029 87 Avenue, Edmonton - (780) 437-4673

Newfoundland : Glencoe Drive, Mount Pearl - (709) 726-6774 Nova Scotia : 25 Raddall Avenue, Dartmouth - (902) 468-4736